## Legend & Protocol
CLASH COORDINATION MATRIX
Legend, priorities, tolerances & coordination protocol
DISCIPLINE CODES
Code | Discipline | Typical model authors / notes
AR | Architecture | Architectural model — spaces, walls, ceilings, finishes, clearances
ST | Structure | Structural model — priority element; gives way last
ME | Mechanical / HVAC | HVAC ducts, AHUs, FCUs, plant
EL | Electrical | Cable trays, busbar, containment, panels
ICT | Info & Communication Technology (ELV) | Data/structured cabling, comms & server rooms, CCTV, access control, AV, telecom containment — segregate from EL power (EMI) & from wet services
PH | Public Health (Plumbing & Drainage) | Gravity drainage (fixed gradient), domestic water, pumps
FF | Fire Fighting / Protection | Sprinkler mains, hydrants, pumps, tanks — Civil Defence approval
FA | Facade / Envelope | Curtain wall, cladding, brackets, slab-edge interface
VT | Vertical Transportation | Lifts, escalators — shaft, pit, overrun, running clearances
CV | Civil / External Works | Below-ground drainage, roads, retaining, site utilities
LS | Landscape | Softscape, hardscape, irrigation, external lighting
CLASH PRIORITY (what gets tested)
P1 | Critical / Hard clash | Life-safety, structural or primary-service conflict. Hard clash, 0mm tolerance. Resolve before issue.
P2 | Major / Hard clash | Physical overlap requiring rework or a clearance breach. Resolve within the coordination cycle.
P3 | Minor / Soft clash | Clearance, access or maintenance-zone breach. Tracked; resolved where practical.
N/A | No meaningful interface | No routine clash test required between this pair.
CLEARANCE / TOLERANCE BASIS
0mm | Hard clash — any geometric overlap is flagged (structure, facade, gravity connections).
25mm | Insulation / cover / installation clearance around ducts, pipes, trays and finishes.
50mm | Service-to-service running clearance for install & maintenance access (incl. EL/ICT segregation).
150mm | Electrical containment clearance below / away from wet services (safety separation).
— | Interface pair — clearance governed by design zone / authority requirement, not a fixed value.
COORDINATION ROLE CODES (RACI)
A | Accountable | Owns the federated model & clash-resolution process; runs detection, chairs coordination, signs off closure. One party only.
R | Responsible | Author of the model in conflict; investigates and proposes / executes the fix.
A · R | Accountable + Responsible | Party both owns the process and authors one of the clashing models.
C | Consulted | Two-way input required before a fix is fixed (e.g. resolution affects ceiling void, riser, or facade intent).
I | Informed | Kept updated on the outcome; no design input required.
GIVE-WAY / RESOLUTION HIERARCHY (highest priority stays put; lower gives way)
Rank | Element | Basis
1 | Architecture (AR) | Absorbs residual via bulkheads / ceiling drops where clearances allow.
2 | Structure (ST) | Moves last — reroute services, never the frame (except designed penetrations).
3 | Gravity drainage (PH) & below-ground civil (CV) | Fixed invert levels / gradients.
4 | Vertical transportation (VT) | Fixed shaft, pit and running clearances — no encroachment.
5 | Large ductwork (ME) | Bulky, low flexibility; other services route around it.
6 | Fire mains & sprinkler (FF) | Coordinated grid; limited flexibility.
7 | Pressurised water pipes (PH) | More flexible than gravity / ducts.
8 | Cable trays / busbar (EL — major) | Reroutable within containment strategy.
9 | Comms & data containment (ICT) | Light, flexible; routes around power & ducts — keep EMI separation from EL.
10 | Conduit / final connections (EL — minor) | Most flexible; gives way first.
THE TWO SCENARIOS — WHAT CHANGES
Aspect | Scenario 1 — As LDC (Lead Design Consultant) | Scenario 2 — As Architect only
Federated model | Architect hosts & maintains the federated model | Hosted by appointed BIM Coordinator / Lead Consultant / Main Contractor
Clash detection | Architect runs detection across ALL pairs | Architect runs detection only on AR-involving pairs; receives clash reports for the rest
Accountability (A) | Architect is Accountable for EVERY pair | Accountability sits with the appointed lead; architect not accountable for non-AR pairs
Non-AR pairs (e.g. ST-ME, ME-ICT) | A — architect owns the process, disciplines are R | I — informed; or C where the fix hits ceiling void / riser / facade
AR-involving pairs | A · R — owns process AND authors AR model | R — resolves its own model's clashes only
Coordination meetings | Architect chairs & tracks to closure | Architect attends & closes its own items
ASSUMPTIONS
• | Generic building project; discipline list & pairs to be trimmed / extended per project scope.
• | ICT = Information & Communication Technology (ELV / low-voltage). Segregate from EL power for EMI and from wet services for water damage.
• | Tolerances are indicative — align to the project BEP, specs and authority (e.g. Civil Defence) requirements.
• | Matrix is symmetric; only the upper-right triangle is populated. Grey cells are mirrors.
• | 'LDC' read as Lead Design Consultant. Adjust accountable-party names on the coordination sheets to match the appointment.

## Clash Test Matrix
CLASH TEST MATRIX — priority · clearance tolerance (applies to both scenarios)
Which discipline pairs are clash-tested, at what priority and clearance. WHO coordinates them is on the two scenario sheets.
Discipline |  | AR | ST | ME | EL | ICT | PH | FF | FA | VT | CV | LS
AR | Architecture | AR | P1 0mm | P2 25mm | P2 25mm | P2 25mm | P2 25mm | P2 25mm | P1 0mm | P1 25mm | P2 — | P3 —
ST | Structure |  | ST | P1 0mm | P1 0mm | P1 0mm | P1 0mm | P1 0mm | P1 0mm | P1 0mm | P1 0mm | P3 —
ME | Mechanical / HVAC |  |  | ME | P2 50mm | P2 50mm | P2 50mm | P2 50mm | P3 25mm | P3 — | P3 — | N/A
EL | Electrical |  |  |  | EL | P2 50mm | P1 150mm | P2 50mm | P3 25mm | P2 25mm | P3 — | P3 —
ICT | Info & Communication Technology (ELV) |  |  |  |  | ICT | P2 50mm | P2 50mm | P3 25mm | P2 25mm | P3 — | P3 —
PH | Public Health (Plumbing & Drainage) | PH: PH; FF: P2 50mm; FA: P3 —; VT: P2 25mm; CV: P1 0mm; LS: P2 —
FF | Fire Fighting / Protection | FF: FF; FA: P3 —; VT: P2 25mm; CV: P3 —; LS: P3 —
FA | Facade / Envelope | FA: FA; VT: N/A; CV: P3 —; LS: P3 —
VT | Vertical Transportation | VT: VT; CV: P3 —; LS: N/A
CV | Civil / External Works | CV: CV; LS: P2 —
LS | Landscape | bar: ME to LS
Key: |  | AR: P1 Critical/hard 0mm; EL: P2 Major; FF: P3 Minor/soft; CV: N/A no interface

## Coordination – As LDC
COORDINATION — SCENARIO 1 : AS LDC (Lead Design Consultant)
Architect is ACCOUNTABLE (A) for every pair — hosts the federated model, runs detection, chairs & closes. Cells show the ARCHITECT's role.
Discipline |  | AR | ST | ME | EL | ICT | PH | FF | FA | VT | CV | LS
AR | Architecture | AR | A · R | A · R | A · R | A · R | A · R | A · R | A · R | A · R | A · R | A · R
ST | Structure | bar: ST to LS
ME | Mechanical / HVAC |  |  | ME | A | A | A | A | A | A | A | N/A
EL | Electrical | bar: ME to LS
ICT | Info & Communication Technology (ELV) |  |  |  |  | ICT | A | A | A | A | A | A
PH | Public Health (Plumbing & Drainage) | bar: ME to LS
FF | Fire Fighting / Protection | bar: ME to LS
FA | Facade / Envelope | FA: FA; VT: N/A; CV: A; LS: A
VT | Vertical Transportation | VT: VT; CV: A; LS: N/A
CV | Civil / External Works | bar: ME to LS
LS | Landscape | bar: ME to LS
Key: |  | AR: A · R accountable + AR author; ICT: A accountable (disciplines are R); VT: N/A no interface

## Coordination – Architect Only
COORDINATION — SCENARIO 2 : AS ARCHITECT ONLY
Accountability (A) sits with the appointed BIM Coordinator / Lead Consultant / Main Contractor. Cells show the ARCHITECT's role only.
Discipline |  | AR | ST | ME | EL | ICT | PH | FF | FA | VT | CV | LS
AR | Architecture | bar: AR to LS
ST | Structure |  | ST | I | I | I | I | I | C | I | I | I
ME | Mechanical / HVAC |  |  | ME | C | C | C | C | C | I | I | N/A
EL | Electrical |  |  |  | EL | C | C | C | C | I | I | I
ICT | Info & Communication Technology (ELV) |  |  |  |  | ICT | C | C | C | I | I | I
PH | Public Health (Plumbing & Drainage) | [5 empty] | PH | C | C | I | I | I
FF | Fire Fighting / Protection |  |  | C: FF; C: C; I: I; I: I; N/A: I
FA | Facade / Envelope |  |  | C: FA; I: N/A; I: C; N/A: C
VT | Vertical Transportation |  |  | I: VT; I: I; N/A: N/A
CV | Civil / External Works | bar: C to N/A
LS | Landscape | bar: C to N/A
Key: |  | R resolves own AR clashes |  | C: C consulted (void/riser/facade); C: I informed; I: N/A no interface